gricultural machinery

Testing

and

1977

นอนอว

aluation

AMTEC

AGRICULTURAL MACHINERY TESTING AND EVALUATION CENTER

Test Report No. 2019-0751

―-

Agricultural Machinery - Solar-Powered Irrigation System Brgy. Pieza, Lamut, Ifugao

College of Engineering and Agro-Industrial Technology, University of the Philippines Los Baños, College, Laguna 4031 Email: amtec.uplb@up.edu.ph Facebook: www.facebook.com/amtec.uplb Website: www.amtec.ceat.uplb.edu.ph Contact Numbers: +63 921 400 7137 (Smart) / +63 977 204 7236 (Globe)

SITY

UNIVER

OF THE

1905

PHILIPPINES

OF THE

LOS BANOS

UNIVERSITY

CEAT

PHILIPPINES

TR No. 2019-0751 (SPIS Brgy. Pieza, Lamut, Ifugao)

Page 2 of 10

Test Report Number

Date of Issuance

Valid Until

Agricultural Machinery

Type

Pump Brand

Pump Model

Photovoltaic Solar Panel Brand

Photovoltaic Solar Panel Model

Test Requested by

2019-0751

November 16, 2019

November 16, 2024

9

Solar-Powered Irrigation System

Submersible Pumpset Powered by 210 Polycrystalline Photovoltaic Modules

MASTRA

8SP95-10

SUNKET

SL315-72P

HEAL THE WORLD ENERGY SAVINGS CORP. 753 Tandang Sora St. Cor. Mindanao Ave., Brgy. Tandang Sora, Quezon City

SUMMARY

Performance Criteria

Manufacturer's Data

AMTEC Test

Discharge Capacity, m3/h

a. Maximum

120

89.07a

b. Average

ND

60.75b

Maximum Total Head, m

210

106.04a

Solar Array Output Voltage, DCV

519.12°

469.73539.73

Solar Array Output Power, W

66150d

7625.34-27616.36

Solar Irradiance, W/m2

ND

171.96-725.30

Ambient Conditions

a. Temperature, °C

b. Relative Humidity, %

PV Module Temperature, °C

ND

26.80-30.00

ND

73.00 -84.00

ND

27.20-44.90

a

Highest observed during test at 699.37 w/m2 irradiance

b Average values of data obtained at 30 minutes interval.

PV module Vmp multiplied by the number of modules/string PV module rated power multiplied by the total number of modules Note: ND - No Data

This is an official document of the Agricultural Machinery Testing and Evaluation Center (AMTEC) of the College of Engineering and Agro-Industrial Technology (CEAT) University of the Philippines Los Baños (UPLB) Falsification of document is punishable by law under Article 172 of the Revised Penal Code.

TR No. 2019-0751 (SPIS Brgy. Pieza, Lamut, Ifugao)

Page 3 of 10

OBSERVATIONS

1. Operator's Manual

2. Previous Valid Test Reports of

Similar Brand and Model

3. PV Module Manufacturer

4. Pumpset Manufacturer

Not Provided

None

WUXI SUNKET NEW ENERGY TECHNOLOGY CO., LTD.

No. 888, Delin Industry Park, Qinghong Road, E'hu Town, Wuxi, Jiangsu

GUANGDONG RUIRONG PUMP INDUSTRY

LTD.

No.22, North 3rd Road, Duruan, Pengjiang, Jiangmen City, Guangdong, China

5. Time of Test

a.

b.

6. Other Remarks

C.

8:00 AM - 3:00 PM

The panels are inclined 11° facing about 225° South East.

The system derives water from an open source river.

System test terminated after 3:00 pm due to overcast and rain

PURPOSE AND SCOPE OF TEST

Purpose

Date of Test

Location of Test

Items Tested

Performance Testing / Commercial

October 6, 2019

Brgy. Pieza, Lamut, Ifugao

16°38'55.39"N. 121°10'35.03"E

Solar Panel Power Output, Input Power to the Pumpset, Pumpset Output Power, Discharge Capacity, Total Head, System Efficiency, and PV Module Temperature

METHODS OF TEST

The solar-powered irrigation system was tested following the AMTEC-DA/BAFE

Solar Powered Irrigation System (SPIS) Testing Protocol.

This is an official document of the Agricultural Machinery Testing and Evaluation Center (AMTEC) of the College of Engineering and Agro-Industrial Technology (CEAT) University of the Philippines Los Baños (UPLB) Falsification of document is punishable by law under Article 172 of the Revised Penal Code.

TR No. 2019-0751 (SPIS Brgy. Pieza, Lamut, Ifugao)

Page 4 of 10

a

b

DESCRIPTION OF THE SYSTEM

Figure 1. Components of the Solar-Powered Irrigation System installed in Barangay Pieza, Lamut, Ifugao include the following: a) PV modules, and b) Discharge pipe and tank.

This is an official document of the Agricultural Machinery Testing and Evaluation Center (AMTEC) of the College of Engineering and Agro-Industrial Technology (CEAT) University of the Philippines Los Baños (UPLB) Falsification of document is punishable by law under Article 172 of the Revised Penal Code.

TR No. 2019-0751 (SPIS Brgy. Pieza, Lamut, Ifugao)

Page 5 of 10

DESCRIPTION OF THE SYSTEM (Cont'n)

b

PF COMBINER BOX

A

a

Figure 2. Inverter (a) and combiner box (b) of the Solar-Powered Irrigation System installed in Barangay Pieza, Lamut, Ifugao.

This is an official document of the Agricultural Machinery Testing and Evaluation Center (AMTEC) of the College of Engineering and Agro-Industrial Technology (CEAT) University of the Philippines Los Baños (UPLB) Falsification of document is punishable by law under Article 172 of the Revised Penal Code.

TR No. 2019-0751 (SPIS Brgy. Pieza, Lamut, Ifugao)

Page 6 of 10

SPECIFICATIONS

1

Reservoir

Item

Manufacturer's Specification

AMTEC Verificationb

1.1 Overall dimensions, mm

1.1.1 Length

ND

9.92

1.1.2 Width

ND

9.90

1.1.3 Height

ND

2.95

1.2

Material of construction

2

Pumpset

2.1

Brand

MASTRA

a

ND

2.2

Model

8SP95-10a

ND

2.3

Serial number

ND

ND

2.4

Type

Submersible

ND

GUANGDONG

ND

2.5

Manufacturer

RUIRONG PUMP

INDUSTRY LTD.

2.6

Country of manufacture

CHINA

ND

2.7

Rated power, kW

45

ND

2.8

Rated voltage, V

380

ND

2.9

Rated current, A

96.9

ND

2.10

Rated frequency, Hz

50

ND

2.11

Rated maximum discharge, m3/h

120

ND

2.12

Rated maximum total head, m

210

ND

3

Controller/Inverter

3.1

Brand

HOBER

HOBER

3.2

Model

HSPH55KH

HSPH55KH

3.3

Enclosure class

ND

ND

3.4

Input

3.4.1 Maximum power, kW

55

55

3.4.2 Maximum input voltage, DCV

400-780

400-780

3.4.3 Maximum input current, DCA

ND

ND

3.5 Output

3.5.1 Maximum power, kW

3.5.2 Maximum output voltage, ACV 3.5.3 Maximum output current, A Note: ND - No Data, NM - Not Measured

ND 380-440d

ND

380-440d

ND

ND

This is an official document of the Agricultural Machinery Testing and Evaluation Center (AMTEC) of the College of Engineering and Agro-Industrial Technology (CEAT) University of the Philippines Los Baños (UPLB) Falsification of document is punishable by law under Article 172 of the Revised Penal Code.

TR No. 2019-0751 (SPIS Brgy. Pieza, Lamut, Ifugao)

SPECIFICATIONS (Cont'n)

Page 7 of 10

Item

Manufacturer's

Specification

AMTEC Verification

4

Solar module

4.1

Brand

4.2

Model

4.3

Manufacturer

4.4

Country of manufacture

4.5

Cell type

Polycrystallinea

4.6

Cell size, L × W, mm

NDa

SUNKETa

SLP315-72a

WUXI SUNKET NEW

ENERGY

TECHNOLOGY CO.,

LTDa

Chinaa

SUNKETa

SLP315-72a

WUXI SUNKET NEW ENERGY TECHNOLOGY

CO., LTDa

China

Polycrystalline

NM

4.7

Cell configuration

72 (6 x 12)a

76 (6 x 12)

4.8

Module dimension, mm

4.8.1 Length

ND

NM

4.8.2 Width

ND

NM

4.9

Total number of solar modules

ND

210

4.9.1 Number of solar modules/string

ND

14

4.9.2 Number of strings

ND

15

4.10

Nominal power, Wp, W

315

270

4.11

Short circuit current, Isc, A

8.93

9.32

4.12

Open circuit voltage, Voc, V

45.24

37.9

4.13

Current at maximum power,

8.50

8.75

Impp, A

4.14

Voltage at maximum power,

37.08

30.8

Vmpp, V

4.15

Temperature condition, T., °C

25

25

4.16

Maximum system current, DCA

ND

119a

4.17 Maximum system voltage, DCV

ND

556b

Nominal operating cell

4.18

25

25

temperature, °C

4.19 Orientation

ND

South East

4.20

Inclination, °

ND

4

5

6

Safety devices

Special features

a PV module Imp multiplied by the number of strings

dbpV module Vmp multiplied by the number of panels/string

ND

ND

315a

ND

Note: ND- No Data

NM - Not Measured

This is an official document of the Agricultural Machinery Testing and Evaluation Center (AMTEC) of the College of Engineering and Agro-Industrial Technology (CEAT) University of the Philippines Los Baños (UPLB) Falsification of document is punishable by law under Article 172 of the Revised Penal Code.

RESULTS

TR No. 2019 – 0751 (SPIS Brgy. Pieza, Lamut, Ifugao)

Table 1. Performance of the Solar- Irrigation System Installed in Brgy. Pieza, Lamut, Ifugao

Ambient Conditions

Solar Panel Output (DC)

Input to the Pumpset

Pumpset Output

Solar

Time of the

Day

Irradiance,

W/m2

Solar

Power, W

Module

Tempe-

Relative

Discharge

Tempe-

Frequency

Total

Output

Humidity,

V

A

Power, W

Capacity,

rature, °C

(Hz)

Head, m

Power, W

System

Efficiency,

%

rature, °C

%

m3/h

8:00 AM

224.73

94388.00

27.20

27.20

80.97

481.60

21.27

10242.03

30.23

56.83

36.42

45.13

4475.71

4.74

8:30 AM

171.96

72224.60

31.55

26.80

84.00

469.73

16.23

7625.34

26.57

49.53

37.20

33.29

3371.82

4.67

9:00 AM

9:30 AM

400.73

168308.00

37.87

27.57

83.80

522.23

33.13

17303.33

34.90

61.80

86.30

77.28

18161.52

10.79

408.43

171542.00

36.05

27.27

81.20

496.60

30.53

15162.85

35.20

65.17

73.59

68.68

13763.84

8.02

10:00 AM 334.37

140434.00

37.27

28.70

82.40

497.27

29.33

14586.49

32.90

60.13

58.67

56.91

9093.03

6.47

10:30 AM 374.47 11:00 AM 416.73 11:30 AM 316.33 12:00 PM

12:30 PM

1:00 PM

157276.00

39.15

28.60

79.20

495.53

34.07

16881.17

37.60

63.63

67.73

64.31

11863.18

7.54

175028.00

41.70

28.90

78.53

482.60

37.20

17952.72

35.60

65.03

68.08

64.58

11973.94

6.84

132860.00

34.63

28.60

77.63

481.87

27.00

13010.40

37.25

58.50

54.95

53.57

8017.23

6.03

321.00

134820.00

35.18

29.70

76.40

487.53

29.27

14268.48

33.40

61.60

55.73

54.29

8239.04

6.11

699.37

293734.00

43.83

29.40

80.33

539.73

51.17

27616.36

41.20

73.40

106.04

89.07

25723.27

8.76

725.30

304626.00

44.90

29.50

79.50

537.13

51.13

27465.42

41.00

68.77

105.29

88.65

25419.06

8.34

1:30 PM

2:00 PM

2:30 PM

3:00 PM

311.17

130690.00

37.55

29.50

75.50

490.27

28.77

14103.34

31.50

58.10

54.12

52.79

7779.98

5.95

374.13

157136.00

37.67

29.90

75.30

499.93

33.90

16947.74

33.60

61.47

65.22

62.35

11075.55

7.05

285.87

120064.00

36.00

30.00

73.70

493.63

25.87

12768.65

30.70

56.47

55.06

53.67

8046.55

6.70

224.80

94416.00

32.55

29.27

73.00

478.43

23.97

11466.45

29.80

54.53

48.02

46.71

6108.02

6.47

Falsification of document is punishable by law under Article 172 of the Revised Penal Code. of Engineering and Agro-Industrial Technology (CEAT) University of the Philippines Los Baños (UPLB)

This is an official document of the Agricultural Machinery Testing and Evaluation Center (AMTEC) of the College

Page 8 of 10

Falsification of document is punishable by law under Article 172 of the Revised Penal Code. of Engineering and Agro-Industrial Technology (CEAT) University of the Philippines Los Baños (UPLB) This is an official document of the Agricultural Machinery Testing and Evaluation Center (AMTEC) of the College

Power (kW). Solar Irradiance (kW/m2), System Efficiency (%)

30.00

25.00

20.00

15.00

10.00

5.00

500

RESULTS (Cont' n)

120.00

100.00

80.00

60.00

40.00

20.00

0.00

0.00

8:00 AM 8:30 AM

9:00 AM

9:30 AM

10:00 AM

10:30 AM

11:00 AM 11:30 AM

12:00 PM

12:30 PM 1:00 PM

1:30 PM

2:00 PM 2:30 PM

3:00 PM

Time of the Day

--Solar Panel Output Power

Pumpset Output Power

System Efficiency

Solar Irradiance

Discharge Capacity

Total Head

Solar Power

-Module Temperature

Figure 3. Performance Characteristic Curves of the Solar-Powered Irrigation System installed in Brgy. Pieza, Lamut, Ifugao

Solar Power (kW). Module Temperature (°C). Total Head (m).

Discharge Capacity (m3/h)

TR No. 2019-0751 (SPIS Brgy. Pieza, Lamut, Ifugao)

Page 9 of 10

TR No. 2019 – 0751 (SPIS Brgy. Pieza, Lamut, Ifugao)

Page 10 of 10

REMINDER

Prepared by:

ALPHONSE REGIN R. MAGMANLAC Test Engineer

Verified by:

ROMULO E. EUSEBIO

MUL

Test Engineer

Approved for Release:

ARTHUR L. FAJARDO AMTEC Director

NOV 16 2019

Date

This test report should not be used for advertisement or for promotion of the product but only for evaluation and verification purposes and should not be reproduced in whole or in part

without the permission of AMTEC.

For inquiries regarding the test report, you can visit us at our office, contact us at +63 921 400 7137 / +63 977 204 7236, send us a message at amtec.uplb@up.edu.ph or visit our official website at www.amtec.ceat.uplb.edu.ph.

This is an official document of the Agricultural Machinery Testing and Evaluation Center (AMTEC) of the College of Engineering and Agro-Industrial Technology (CEAT) University of the Philippines Los Baños (UPLB) Falsification of document is punishable by law under Article 172 of the Revised Penal Code.